## Step 1
| Wind speed (m/s) | Power output (kW)
| 0 | 0
| 1 | 0
| 2 | 0
| 3 | 20
| 4 | 90
| 5 | 130
| 6 | 390
| 7 | 650
| 8 | 920
| 9 | 1280
| 10 | 1540
| 11 | 1890
| 12 | 1970
| 13 | 1980
| 14 | 1990
| 15 | 2000
| 16 | 2000
| 17 | 2000
| 18 | 2000
| 19 | 2000
| 20 | 2000
| 21 | 0
| 22 | 0
| 23 | 0
| 24 | 0
| 25 | 0
Power starts to be generated at 3m/s. The values at the power output column are real based on the performance of the specific 2MW wind turbine. At 15m/s we actually reach full peak output. From that point (wind speed) up to the cut-out speed (21m/s) we are getting 2MW. From 21m/s the wind turbine stops operating so the output is going to be zero. This is how you’re interpreting the curve. When you are looking to install a wind turbine a similar graph (specification sheet, will be available to you). Once you have the power curve you have the power output at each speed.
Cut-in speed: 3m/s
Cut-out speed: 21m/s
wind speed m/s
Power kW

## Step 2
| Wind speed (m/s) | Power output (kW) | Wind speed (m/s) | hrs/y | Output (kWh/yr)
| 0 | 0 | 0 | 450 | 0
| 1 | 0 | 1 | 400 | 0
| 2 | 0 | 2 | 700 | 0
| 3 | 20 | 3 | 1200 | 24000
| 4 | 90 | 4 | 750 | 67500
| 5 | 130 | 5 | 1200 | 156000
| 6 | 390 | 6 | 900 | 351000
| 7 | 650 | 7 | 640 | 416000
| 8 | 920 | 8 | 220 | 202400
| 9 | 1280 | 9 | 450 | 576000
| 10 | 1540 | 10 | 300 | 462000
| 11 | 1890 | 11 | 200 | 378000
| 12 | 1970 | 12 | 150 | 295500
| 13 | 1980 | 13 | 250 | 495000
| 14 | 1990 | 14 | 300 | 597000
| 15 | 2000 | 15 | 100 | 200000
| 16 | 2000 | 16 | 50 | 100000
| 17 | 2000 | 17 | 150 | 300000
| 18 | 2000 | 18 | 50 | 100000
| 19 | 2000 | 19 | 100 | 200000
| 20 | 2000 | 20 | 75 | 150000
| 21 | 0 | 21 | 125 | 0
| 22 | 0 | 22 | 0 | 0
| 23 | 0 | 23 | 0 | 0
| 24 | 0 | 24 | 0 | 0
| 25 | 0 | 25 | 0 | 0
|  |  | total hrs/yr | 8760
|  |  | total kWh/yr |  | 5070400
How do we determine the actual kWh given different length of time at different wind speeds? A column has been added with hypothetical hours per year (wind speed profile for the year). For example, you have 450 hours per year with no wind. And if you sum all the numbers you get the number of hours in a year which is 8760h. We want to determine the output in kWh of this turbine under these conditions we simply take the kW times (X) the hours per year (yellow column) and that will result in kWh /yr. (green column). Finally, I can see the total output under these specific conditions at this location.
Cut-in speed: 3m/s
Cut-out speed: 21m/s
Wind speed m/s
Power kW

## Step 3
| Wind speed (m/s) | Power output (kW) |  | Wind speed (m/s) | hrs/y | Output (kWh/yr)
| 0 | 0 |  | 0 | 450 | 0
| 1 | 0 |  | 1 | 400 | 0
| 2 | 0 |  | 2 | 700 | 0
| 3 | 20 |  | 3 | 1200 | 24000
| 4 | 90 |  | 4 | 750 | 67500
| 5 | 130 |  | 5 | 1200 | 156000
| 6 | 390 |  | 6 | 900 | 351000
| 7 | 650 |  | 7 | 640 | 416000
| 8 | 920 |  | 8 | 220 | 202400
| 9 | 1280 |  | 9 | 450 | 576000
| 10 | 1540 |  | 10 | 300 | 462000
| 11 | 1890 |  | 11 | 200 | 378000
| 12 | 1970 |  | 12 | 150 | 295500
| 13 | 1980 |  | 13 | 250 | 495000
| 14 | 1990 |  | 14 | 300 | 597000
| 15 | 2000 |  | 15 | 100 | 200000
| 16 | 2000 |  | 16 | 50 | 100000
| 17 | 2000 |  | 17 | 150 | 300000
| 18 | 2000 |  | 18 | 50 | 100000
| 19 | 2000 |  | 19 | 100 | 200000
| 20 | 2000 |  | 20 | 75 | 150000
| 21 | 0 |  | 21 | 125 | 0
| 22 | 0 | maximum possible output = number hrs in a year X maximum output power | 22 | 0 | 0
| 23 | 0 | maximum possible output = 8760 X 2000 | 23 | 0 | 0
| 24 | 0 |  | 24 | 0 | 0
| 25 | 0 |  | 25 | 0 | 0
|  |  |  | total hrs/yr | 8760
|  |  |  | total kWh/yr |  | 5070400
|  |  |  | max output |  | 17520000
Last thing is to calculate the capacity factor under these conditions. In order to do that I need to determine the maximum possible power output of this turbine (max possible output X number of hrs/y). As you can see the capacity factor it tells you what percent of the maximum possible output you are actually getting. If we would be operating at the peak output all year (8760 X 2000 = 17.5 GWhrs/yr.
Cut-in speed: 3m/s
Cut-out speed: 21m/s
Wind speed m/s
Power kW

## Step 4
| Wind speed (m/s) | Power output (kW) |  | Wind speed (m/s) | hrs/y | Output (kWh/yr)
| 0 | 0 |  | 0 | 450 | 0
| 1 | 0 |  | 1 | 400 | 0
| 2 | 0 |  | 2 | 700 | 0
| 3 | 20 |  | 3 | 1200 | 24000
| 4 | 90 |  | 4 | 750 | 67500
| 5 | 130 |  | 5 | 1200 | 156000
| 6 | 390 |  | 6 | 900 | 351000
| 7 | 650 |  | 7 | 640 | 416000
| 8 | 920 |  | 8 | 220 | 202400
| 9 | 1280 |  | 9 | 450 | 576000
| 10 | 1540 |  | 10 | 300 | 462000
| 11 | 1890 |  | 11 | 200 | 378000
| 12 | 1970 |  | 12 | 150 | 295500
| 13 | 1980 |  | 13 | 250 | 495000
| 14 | 1990 |  | 14 | 300 | 597000
| 15 | 2000 |  | 15 | 100 | 200000
| 16 | 2000 |  | 16 | 50 | 100000
| 17 | 2000 |  | 17 | 150 | 300000
| 18 | 2000 |  | 18 | 50 | 100000
| 19 | 2000 |  | 19 | 100 | 200000
| 20 | 2000 |  | 20 | 75 | 150000
| 21 | 0 |  | 21 | 125 | 0
| 22 | 0 | maximum possible output = number hrs in a year X maximum output power | 22 | 0 | 0
| 23 | 0 | maximum possible output = 8760 X 2000 | 23 | 0 | 0
| 24 | 0 |  | 24 | 0 | 0
| 25 | 0 |  | 25 | 0 | 0
|  |  |  | total hrs/yr | 8760
|  |  |  | total kWh/yr |  | 5070400
|  |  |  | max output |  | 17520000
|  |  | Caparity factor: total (actual) output / max output | Capacity factor |  | 28.94% | 0.28
The capacity factor is simply the actual output divided by the maximum possible output (and we make it as a percentage which is 28.94%. For most wind turbines if you are getting a 40% capacity factor you are doing really well for the utility scale, for the residential scale is much lower.This concludes the demonstration on how to calculate output and capacity factor of a wind turbine.
Cut-in speed: 3m/s
Cut-out speed: 21m/s
Wind speed m/s
Power kW