## CoolingTower
CALCULATION OF WATER VAPOUR PRESSURE | [6 empty] | CALCULATION OF INTERFACIAL WET ENTHALPY |  |  |  |  | (design) | INTEGRATION | [7 empty] | CALCULATION OF INTERFACIAL WET ENTHALPY |  |  |  |  | (new) | INTEGRATION
Tc= | 647.096 | K |  |  |  | T | θ |  | Pws | w_sat | H_i | H | int_dTL_des | Design conditions | [5 empty] | T | θ |  | Pw_sat | w_sat | H_i | H |  | New conditions
Pc= | 22064 | kPa |  |  |  | 20.3 | 0.54651 | -4.1419 | 2.383 | 0.01498 | 58.5275 |  |  | T_L | H | H_max | T_L1= | 26 | [9 empty] | T_L | H | T_L1= | 26
C1= | -7.8595 |  | P= | 101.33 | kPa | [8 empty] | 26 | 58.4 | 58.4 | H_1= | 58.4 | [8 empty] | 4.7962 | 26 | 58.4 | H_1= | 58.4
C2= | 1.8441 |  | T= | 28 | [8 empty] | 2.6729 | 27 | 62.945 | 65.975 | G_B= | 800 | kg/h | [8 empty] | 27 | 64.67 | G_B= | 800 | kg/h
C3= | -11.7866 |  | θ= | 0.53461 | [9 empty] | 28 | 67.49 | 73.55 | L= | 869.8565 | kg/h | [8 empty] | 28 | 70.94 | L= | 1200 | kg/h
C4= | 22.6807 |  |  | -4.0355 |  | 26 | 0.5377 | -4.063 | 3.3638 | 0.021357 | 80.7015 | 58.4 | 0.044907 | 29 | 72.035 | 81.125 | Cp,L= | 4.18 | kJ/kgK | 26 | 0.5377 | -4.063 | 3.3638 | 0.021357 | 80.7015 | 58.4 | 0.046798 | 29 | 77.21 | Cp,L= | 4.18 | kJ/kgK
C5= | -15.9619 |  | RH%= | 50 |  | 27 | 0.53616 | -4.0492 | 3.568 | 0.022701 | 85.1805 | 62.945 | 0.044838 | 30 | 76.58 | 88.7 | ratio= | 4.545 |  | 27 | 0.53616 | -4.0492 | 3.568 | 0.022701 | 85.1805 | 64.67 | 0.050805 | 30 | 83.48 | ratio= | 6.27
C6= | 1.8012 |  | PA= | 1.8915 | kPa | 28 | 0.53461 | -4.0355 | 3.783 | 0.024121 | 89.8601 | 67.49 | 0.044362 | 31 | 81.125 | 96.275 | ratio_max= | 7.575 |  | 28 | 0.53461 | -4.0355 | 3.783 | 0.024121 | 89.8601 | 70.94 | 0.054931 | 31 | 89.75
|  |  | w= | 0.011831 | g A/kgB | 29 | 0.53307 | -4.0217 | 4.0091 | 0.025623 | 94.7513 | 72.035 | 0.043483 | 32 | 85.67 | 103.85 | L_max= | 1449.7608 | kg/h | 29 | 0.53307 | -4.0217 | 4.0091 | 0.025623 | 94.7513 | 77.21 | 0.059019 | 32 | 96.02
|  |  | H= | 58.4844 | kJ/kgB | 30 | 0.53152 | -4.0081 | 4.2469 | 0.027209 | 99.8655 | 76.58 | 0.042228 | 33 | 90.215 | 111.425 | ratio/ratio_max | 0.6 |  | 30 | 0.53152 | -4.0081 | 4.2469 | 0.027209 | 99.8655 | 83.48 | 0.062846 | 33 | 102.29
|  |  | ratio=-0,41 | -0.40891 |  | 31 | 0.52998 | -3.9944 | 4.4969 | 0.028885 | 105.2149 | 81.125 | 0.040642 | 34 | 94.76 | 119 | T_L2= | 48 |  | 31 | 0.52998 | -3.9944 | 4.4969 | 0.028885 | 105.2149 | 89.75 | 0.066132 | 34 | 108.56 | T_L2= | 50
[6 empty] | 32 | 0.52843 | -3.9808 | 4.7596 | 0.030655 | 110.8124 | 85.67 | 0.038786 | 35 | 99.305 | 126.575 | H_2= | 158.39 |  | 32 | 0.52843 | -3.9808 | 4.7596 | 0.030655 | 110.8124 | 96.02 | 0.068568 | 35 | 114.83 | H_2= | 167.48
[6 empty] | 33 | 0.52689 | -3.9672 | 5.0354 | 0.032525 | 116.6714 | 90.215 | 0.036727 | 36 | 103.85 | 134.15 |  |  |  | 33 | 0.52689 | -3.9672 | 5.0354 | 0.032525 | 116.6714 | 102.29 | 0.069864 | 36 | 121.1
[6 empty] | 34 | 0.52534 | -3.9536 | 5.3251 | 0.0345 | 122.8064 | 94.76 | 0.034535 | 37 | 108.395 | 141.725 | C_tower= | 2.858 |  | 34 | 0.52534 | -3.9536 | 5.3251 | 0.0345 | 122.8064 | 108.56 | 0.069812 | 37 | 127.37 | HTU= | 2.0663
[6 empty] | 35 | 0.5238 | -3.94 | 5.6291 | 0.036585 | 129.2327 | 99.305 | 0.032275 | 38 | 112.94 | 149.3 |  |  |  | 35 | 0.5238 | -3.94 | 5.6291 | 0.036585 | 129.2327 | 114.83 | 0.068349 | 38 | 133.64
[6 empty] | 36 | 0.52225 | -3.9265 | 5.948 | 0.038787 | 135.9663 | 103.85 | 0.030007 | 39 | 117.485 | 156.875 |  |  |  | 36 | 0.52225 | -3.9265 | 5.948 | 0.038787 | 135.9663 | 121.1 | 0.065573 | 39 | 139.91
[6 empty] | 37 | 0.5207 | -3.9129 | 6.2824 | 0.041112 | 143.0246 | 108.395 | 0.027777 | 40 | 122.03 | 164.45 |  |  |  | 37 | 0.5207 | -3.9129 | 6.2824 | 0.041112 | 143.0246 | 127.37 | 0.061727 | 40 | 146.18 | T_L1 | HTU
[6 empty] | 38 | 0.51916 | -3.8994 | 6.633 | 0.043567 | 150.4256 | 112.94 | 0.025622 | 41 | 126.575 | 172.025 |  |  |  | 38 | 0.51916 | -3.8994 | 6.633 | 0.043567 | 150.4256 | 133.64 | 0.057141 | 41 | 152.45 | 26 | 4.7962
[6 empty] | 39 | 0.51761 | -3.886 | 7.0003 | 0.046159 | 158.1888 | 117.485 | 0.023569 | 42 | 131.12 | 179.6 |  |  |  | 39 | 0.51761 | -3.886 | 7.0003 | 0.046159 | 158.1888 | 139.91 | 0.052162 | 42 | 158.72 | 27 | 3.4431
[6 empty] | 40 | 0.51607 | -3.8725 | 7.3851 | 0.048895 | 166.3349 | 122.03 | 0.021635 | 43 | 135.665 | 187.175 |  |  |  | 40 | 0.51607 | -3.8725 | 7.3851 | 0.048895 | 166.3349 | 146.18 | 0.047094 | 43 | 164.99 | 28 | 2.6382
[6 empty] | 41 | 0.51452 | -3.8591 | 7.788 | 0.051785 | 174.8858 | 126.575 | 0.019829 | 44 | 140.21 | 194.75 |  |  |  | 41 | 0.51452 | -3.8591 | 7.788 | 0.051785 | 174.8858 | 152.45 | 0.04217 | 44 | 171.26 | 29 | 2.0998
[6 empty] | 42 | 0.51298 | -3.8457 | 8.2098 | 0.054837 | 183.8651 | 131.12 | 0.018155 | 45 | 144.755 | 202.325 |  |  |  | 42 | 0.51298 | -3.8457 | 8.2098 | 0.054837 | 183.8651 | 158.72 | 0.037548 | 45 | 177.53 | 30 | 1.7433
[6 empty] | 43 | 0.51143 | -3.8323 | 8.6511 | 0.05806 | 193.2977 | 135.665 | 0.016612 | 46 | 149.3 | 209.9 |  |  |  | 43 | 0.51143 | -3.8323 | 8.6511 | 0.05806 | 193.2977 | 164.99 | 0.033312 | 46 | 183.8
[6 empty] | 44 | 0.50989 | -3.819 | 9.1127 | 0.061464 | 203.2104 | 140.21 | 0.015196 | 47 | 153.845 | 217.475 |  |  |  | 44 | 0.50989 | -3.819 | 9.1127 | 0.061464 | 203.2104 | 171.26 | 0.029499 | 47 | 190.07 | 29.1 | 2.0557
[6 empty] | 45 | 0.50834 | -3.8056 | 9.5953 | 0.065059 | 213.6321 | 144.755 | 0.0139 | 48 | 158.39 | 225.05 |  |  |  | 45 | 0.50834 | -3.8056 | 9.5953 | 0.065059 | 213.6321 | 177.53 | 0.026107 | 48 | 196.34
[6 empty] | 46 | 0.5068 | -3.7923 | 10.0998 | 0.068859 | 224.5933 | 149.3 | 0.012717 | [6 empty] | 46 | 0.5068 | -3.7923 | 10.0998 | 0.068859 | 224.5933 | 183.8 | 0.023113 | 49 | 202.61
[6 empty] | 47 | 0.50525 | -3.779 | 10.6269 | 0.072873 | 236.1271 | 153.845 | 0.01164 | [6 empty] | 47 | 0.50525 | -3.779 | 10.6269 | 0.072873 | 236.1271 | 190.07 | 0.020485 | 50 | 208.88
[6 empty] | 48 | 0.50371 | -3.7658 | 11.1775 | 0.077117 | 248.269 | 158.39 | [7 empty] | 48 | 0.50371 | -3.7658 | 11.1775 | 0.077117 | 248.269 | 196.34 | 0.018183 | 51
[6 empty] | 49 | 0.50216 | -3.7525 | 11.7524 | 0.081604 | 261.0571 | [8 empty] | 49 | 0.50216 | -3.7525 | 11.7524 | 0.081604 | 261.0571 | 202.61 | 0.016171 | 52
[6 empty] | 50 | 0.50062 | -3.7393 | 12.3525 | 0.086349 | 274.5327 | [8 empty] | 50 | 0.50062 | -3.7393 | 12.3525 | 0.086349 | 274.5327 | 208.88 |  | 53
[6 empty] | 51 | 0.49907 | -3.7261 | 12.9786 | 0.091369 | 288.7401 | [8 empty] | 51 | 0.49907 | -3.7261 | 12.9786 | 0.091369 | 288.7401
[6 empty] | 52 | 0.49752 | -3.7129 | 13.6318 | 0.096682 | 303.7274 | [8 empty] | 52 | 0.49752 | -3.7129 | 13.6318 | 0.096682 | 303.7274
[6 empty] | 53 | 0.49598 | -3.6998 | 14.3129 | 0.10231 | 319.5468 | [8 empty] | 53 | 0.49598 | -3.6998 | 14.3129 | 0.10231 | 319.5468
[6 empty] | 54 | 0.49443 | -3.6867 | 15.0229 | 0.10827 | 336.2546 | [8 empty] | 54 | 0.49443 | -3.6867 | 15.0229 | 0.10827 | 336.2546
[6 empty] | 55 | 0.49289 | -3.6735 | 15.7628 | 0.11458 | 353.9123 | [8 empty] | 55 | 0.49289 | -3.6735 | 15.7628 | 0.11458 | 353.9123
[6 empty] | 56 | 0.49134 | -3.6605 | 16.5337 | 0.12128 | 372.5869 | [8 empty] | 56 | 0.49134 | -3.6605 | 16.5337 | 0.12128 | 372.5869
[6 empty] | 57 | 0.4898 | -3.6474 | 17.3365 | 0.12838 | 392.3514 | [8 empty] | 57 | 0.4898 | -3.6474 | 17.3365 | 0.12838 | 392.3514
[6 empty] | 58 | 0.48825 | -3.6343 | 18.1723 | 0.13592 | 413.2857 | [8 empty] | 58 | 0.48825 | -3.6343 | 18.1723 | 0.13592 | 413.2857
[6 empty] | 59 | 0.48671 | -3.6213 | 19.0422 | 0.14393 | 435.4774 | [8 empty] | 59 | 0.48671 | -3.6213 | 19.0422 | 0.14393 | 435.4774
[6 empty] | 60 | 0.48516 | -3.6083 | 19.9474 | 0.15245 | 459.0227 | [8 empty] | 60 | 0.48516 | -3.6083 | 19.9474 | 0.15245 | 459.0227
H=H_1+(Lc_(p,L))/G_B (T_L−T_L1 )
𝑤=(𝑀_𝐴/𝑀_𝐵 )∗𝑝_𝐴/〖𝑃−𝑝〗_𝐴
(𝑤_𝑠𝑎𝑡−𝑤)/(𝑇_𝑠𝑎𝑡−𝑇)=−0,41∗〖10〗^(−3)
𝐻=(1.01+1.89𝑤)𝑇+2500𝑤